Q:	What is the Voluntary Replacement Program (VRP)?

A:	It is a program funded by the Tyco Corporation that will pay to replace the 35,000,000 Model “GB” fire sprinkler heads with O-ring water seals manufactured by the Central Sprinkler Company from 1988 to 2000.

Q:	Why are the O-ring fire sprinkler heads being replaced?

A:	The defect with the Model “GB” fire sprinkler head lies with the O-ring which seals the unit in the closed position under non-fire conditions. Underwriters Laboratory tests have revealed that many of these O-ring heads may leak or not operate in a fire because they may require a higher water pressure to operate than is available in some buildings.

Q:	Are O-ring fire sprinkler heads hard to identify?

A:	Yes, there are 65 different models of O-ring heads. Some heads are even covered with a ceiling plate for aesthetic purposes. If you are having difficulty determining whether or not you have O-ring heads, contact our toll free information line at 1-866-WSP-SFMO (1-866-977-7366).

Q:	How can I tell if my residence or facility has O-ring fire sprinkler heads?

A:	First, go to www.sprinklerreplacement.com, select “What Sprinklers are Involved?”, and download the ID Brochure that will assist you in identifying the Model “GB” O-ring heads. You can also download a claim packet at the same website by selecting “How Do I Participate?” If you are still not sure, contact us toll free at 1-866-977-7366.

Q:	Is it going to cost me any money to replace the O-ring fire sprinkler heads?

A:	No. You will not be charged by the Central Sprinkler Company or its designated contractor for the replacement work. However, certain indirect and additional expenses may not be covered by the VRP.

Q:	If I do have Model “GB” O-ring heads, how do I go about getting them replaced?

A:	Fill out the claim form accompanied by close up photos of each model of “GB” fire sprinkler head in your facility and submit it to the Tyco Corporation. Keep a copy of the submitted claim form for your records.

Q:	How long will it take before my O-ring fire sprinkler heads are replaced?

A:	Due to the large number of claims already filed, the expected wait is between 2 and 3 years from the time the claim form has been successfully filed until the heads are replaced.

Q:	How many Model “GB” O-ring sprinkler heads are there in Washington State?

A:	It is estimated that there were over 1.5 million originally installed in Washington State. Over 800,000 have been identified since the VRP was announced in August 2001. It is believed that the majority of the remaining O-ring heads are in hotels, motels, apartments, and residences.

Q:	Do all fire sprinkler heads have O-ring water seals?

A:	No, only two companies (Central Sprinkler Company and Reliable) manufactured fire sprinkler heads with internal O-ring water seals. The other manufacturers use the Belleville Spring water seal. The major difference in the two designs is that no part of the Belleville Spring seal is in contact with the walls of the sprinkler orifice.

Q:	Will my replacement sprinkler heads have O-ring water seals?

A:	No, Underwriters Laboratories will no longer “list” a fire sprinkler head that uses O-ring water seals. All fire sprinkler heads are now manufactured with the Belleville Spring water seal.

Q:	Have there been other recalls of sprinkler heads?

A:	Yes, another O-ring head, the “Omega”, also manufactured by the Central Sprinkler Company, was recalled in 1998. Of the 8 million Omega heads manufactured only 5 million have been located. Unfortunately that recall ended several years ago.

Q:	Why all the recalls on defective fire sprinkler heads?

A:	The issue is not about defective fire sprinkler heads. The issue is about a design flaw in a certain type of fire sprinkler head water seal that is no longer manufactured.  The track record of fire sprinklers over the years has been excellent.